# Recessed mounting louvre DucoGrille Acoustic N 150

Manufactured by: DUCO Ventilation & Sun Control

The DucoGrille Acoustic N150 is a sound-absorbing built-in wall louvre, manufactured from extruded aluminium sections. The louvre blades can be clipped onto plastic blade holders quickly and simply, and are fitted on the inside with sound-absorbing, non-flammable mineral wool. Thanks to its heavy-duty construction, the DucoGrille Acoustic N150 has a high attenuation value plus a low resistance factor (and can consequently supply larger flow rates).

## Features:

* Louvre pitch: 150 mm
* Frame rebate: 0 mm
* Installation depth: 165 mm
* Section thickness: minimum 1.5 mm
* Visual free area: 74 %
* Physical free area: 35%

## Accessories (included):

* Insect-resistant stainless steel mesh 2.3 x 2.3 mm (standard) or vermin-resistant mesh (on request)
* Fixing lugs

## Surface treatment:

* Anodisation: Qualanod-compliant, coating thickness 15-20µm, standard natural colour (colourless anodisation)
* Powder coating: Qualicoat Seaside type A compliant, minimum average coating thickness 60µm, standard RAL colours 70% gloss

Upon request: other finish coating thicknesses, anodising colours and paint gloss levels, textured paints and specific powder coating product codes

## Functional specifications:

### Flow rate:

* + K-factor inlet: 11.49
	+ K-factor outlet: 11.41
	+ Ce coefficient: 0.295
	+ Cdcoefficient: 0.296

### Water resistance:

* + v = 0.0m/s: class B
	+ v = 0.5m/s: class C
	+ v = 1.0m/s: class C
	+ v = 1,5m/s: class C
	+ v = 2.0m/s: class D
	+ v = 2.5m/s: class D
	+ v = 3.0m/s: class D
	+ v = 3.5m/s: class D

### Attenuation value

* + Rw (C;Ctr) (in dB): 11 (-1;-2)

## Complies with or tested in accordance with the following standards:

* Qualicoat Seaside type A (if painted finish)
* Qualanod (if anodised finish)
* EN 573 - EN AW-6063 T66 and EN AW-6060 T66: aluminium alloy & hardening
* EN 13030: water resistance and determination of Ce and Cd coefficients
* EN ISO 10140: acoustic measurements (for acoustic products)