# Wall louvre – DUCO Ventilation & Sun Control
DucoGrille Solid G 30Z Large

## Description

DucoGrille Solid G 30Z Large is a recessed wall louvre made of aluminium extrusion profiles with an extra large flange. The louvre blades offer high ventilation capacity with relatively small louvre blades. The ‘stackable’ louvre blades form a single whole, making them extra strong. The louvre blades are available with small punching (P1), large punching (P2) or as false louvres (NP).

## Version

- Shape of blade	30Z

- Punching		NP – not punched

P1 – height 21 mm x width 2,5 mm

P2 – height 21 mm x width 18 mm

- Pitch			37,5 mm

- Frame width		56 mm

- Flange depth		40 mm

- Frame depth		38 mm

- Mesh			Punching

P1 as insect mesh

P2 as rodent mesh

Stainless-steel mesh

2,3 x 2,3 mm as insect mesh

6 x 6 mm as rodent mesh

20 x 20 mm as bird mesh

- Drip tray profile	Optional

The following combinations are available:

|  | NP | P1 | P1 Incl mesh | P1 + options | P1 Incl mesh + options | P2 | P2 + options |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Punching P1 | - | S | S | S | S | - | - |
| Punching P2 | - | - | - | - | - | S | S |
| Stainless-steel mesh 2,3 x 2,3 | - | - | S | - | S | S | S |
| Stainless-steel mesh 6 x 6 | - | - | - | - | O | - | O |
| Stainless-steel mesh 20x20 | - | - | - | - | O | - | O |
| Drip tray profile | - | - | - | S | S | - | S |

S = standard		O = optional

## Material and surface treatment

- Aluminium		EN AW-6063 T66 (EN 573-3)

Profile thickness: min. 1,5 mm

- Finish

  - Natural anodised (15-20 μm) according to Qualanod

  - Polyester powder coated (60-80 μm) according to Qualicoat Seaside type A (specific RAL codes or textured paint on request)

## Technical specifications

### Reaction to fire

AS-s1,d0 (EN 13501-1)

### Fall-through protection

Class XI (BS 6180)

### Free area

|  | NP | P1 P1 incl mesh P1 + options P1 incl mesh + options | P2 P2 + options |
| --- | --- | --- | --- |
| Visual free area (Per metre punching) | 0 % | 60 % | 86 % |
| Physical free area | 0 % | 34 % | 48 % |

### Airflow data

| EN 13030 | NP | P1 | P1 Incl mesh | P1 + options | P1 Incl mesh + options | P2 | P2 + options |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Ce | - | 0,243 | 0,233 | 0,216 | 0,21 | 0,258 | 0,232 |
| K-factor intake | - | 16,94 | 18,42 | 21,43 | 22,68 | 15,02 | 18,58 |
| Cd | - | 0,234 | 0,224 | 0,242 | 0,226 | 0,253 | 0,266 |
| K-factor exhaust | - | 18,26 | 19,93 | 17,08 | 19,58 | 15,62 | 14,13 |

### Water resistance

| EN 13030 | NP | P1 | P1 Incl mesh | P1 + options | P1 Incl mesh + options | P2 | P2 + options |
| --- | --- | --- | --- | --- | --- | --- | --- |
| V = 0 m/s | - | B | C | B | A | C | B |
| V = 0,5 m/s | - | C | C | B | B | C | B |
| V = 1 m/s | - | C | C | C | B | C | B |
| V = 1,5 m/s | - | D | C | C | B | D | B |
| V = 2 m/s | - | D | D | D | B | D | C |
| V = 2,5 m/s | - | D | D | D | C | D | D |
| V = 3 m/s | - | D | D | D | D | D | D |
| V = 3,5 m/s | - | D | D | D | D | D | D |