# Louvre wall system DUCO Ventilation & Sun Control DucoWall Screening 35

## Description

DucoWall Screening 35 is a sturdy aluminum louvre wall system with a choice between three different louvre pitches. In this way, the louvre wall can be adapted to the wishes and needs of any project. Installation is quick, as the Z-shaped louvre blades are placed directly on the mullion.  
The 'Z'-shaped louvre blade produces a sleek design.

## Version

### Blade

* Shape of blade Z-shaped
* Pitch 75 mm

112.5 mm

150 mm

* Blade height 116 mm
* Blade depth 44 mm

### Mullion

* Mullion 40/21 (Double)
  + Fixing directly to the underlying structure.
  + Without free span.
* Mullion 40/70 Double and 40/100 Double
  + Fixing to the underlying structure with the supplied L-profiles.
  + Suitable for free span.

|  |  |
| --- | --- |
| Type | Installation depth (mm) |
| 40/21 (Double) | 57 |
| 40/70 Double | 107 |
| 40/100 Double | 137 |

### Accessories (+options)

* Insect mesh frame 2.3 x 2.3 mm

## Material and surface treatment

### Blade

* Aluminium EN AW-6063 T66 (EN 573-3)

Profile thickness: min. 2 mm

* Finish
  + Natural anodised (15-20 μm) according to Qualanod
  + Polyester powder coated (60-80 μm) according to Qualicoat Seaside type A (specific RAL codes or textured paint on request)

### Mullions

* Aluminium EN AW-6063 T66 (EN 573-3)

Profile thickness: min. 1.5 mm

* Finish
  + Polyester powder coated (60-80 μm) according to Qualicoat Seaside type A (specific RAL codes or textured paint on request)

## Technical specifications

### Reaction to fire

AS-s1,d0 (EN 13501-1)

### Free area

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Feature | Pitch 75 | | Pitch 112 | | Pitch 150 | |
| **STD** | **+OPT** | **STD** | **+OPT** | **STD** | **+OPT** |
| Visual free area | 52 % | 52 % | 68 % | 68 % | 76 % | 76 % |
| Physical free area | 29 % | 29 % | 27 % | 27 % | 35 % | 35 % |

### Flow rates

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Feature | Pitch 75 | | Pitch 112 | | Pitch 150 | |
| **STD** | **+OPT** | **STD** | **+OPT** | **STD** | **+OPT** |
| Ce | 0.128 | 0.128 | 0.122 | 0.121 | 0.206 | 0.204 |
| K-factor intake | 61.04 | 61.04 | 67.19 | 68.30 | 23.56 | 24.03 |
| Cd | 0.162 | 0.161 | 0.174 | 0.175 | 0.224 | 0.222 |
| K-factor exhaust | 38.10 | 38.58 | 33.03 | 32.65 | 19.93 | 20.29 |

According to EN 13030

### Water resistance

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Velocity v (m/s) | Pitch 75 | | Pitch 112 | | Pitch 150 | |
| **STD** | **+OPT** | **STD** | **+OPT** | **STD** | **+OPT** |
| 0 | B | B | A | A | C | B |
| 0.5 | C | B | B | A | D | C |
| 1 | C | C | C | A | D | C |
| 1.5 | D | C | C | B | D | D |
| 2 | D | D | D | C | D | D |
| 2.5 | D | D | D | D | D | D |
| 3 | D | D | D | D | D | D |
| 3.5 | D | D | D | D | D | D |

According to EN 13030

### Strength calculation

According to EN 1990, EN 1991, EN 1999