# Louvre wall system DUCO Ventilation & Sun Control DucoWall Screening 70

## Description

DucoWall Screening 70 is a sturdy aluminum louvre wall system with a choice between three different louvre pitches. In this way, the louvre wall can be adapted to the wishes and needs of any project. Installation is quick, as the Z-shaped louvre blades are placed directly on the mullion.  
The 'Z'-shaped louvre blade produces a sleek design.

## Version

### Blade

* Shape of blade Z-shaped
* Pitch 75 mm

112.5 mm

150 mm

* Blade height 113 mm
* Blade depth 82 mm

### Mullion

* Mullion 40/21 (Double)
  + Fixing directly to the underlying structure.
  + Without free span.
* Mullion 40/70 Double and 40/100 Double
  + Fixing to the underlying structure with the supplied L-profiles.
  + Suitable for free span.

|  |  |
| --- | --- |
| Type | Installation depth (mm) |
| 40/21 (Double) | 94.5 |
| 40/70 Double | 145 |
| 40/100 Double | 175 |

### Accessories (+options)

* Insect mesh frame 2.3 x 2.3 mm

## Material and surface treatment

### Blade

* Aluminium EN AW-6063 T66 (EN 573-3)

Profile thickness: min. 2 mm

* Finish
  + Natural anodised (15-20 μm) according to Qualanod
  + Polyester powder coated (60-80 μm) according to Qualicoat Seaside type A (specific RAL codes or textured paint on request)

### Mullions

* Aluminium EN AW-6063 T66 (EN 573-3)

Profile thickness: min. 1.5 mm

* Finish
  + Polyester powder coated (60-80 μm) according to Qualicoat Seaside type A (specific RAL codes or textured paint on request)

## Technical specifications

### Reaction to fire

AS-s1,d0 (EN 13501-1)

### Free area

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Feature | Pitch 75 | | Pitch 112 | | Pitch 150 | |
| **STD** | **+OPT** | **STD** | **+OPT** | **STD** | **+OPT** |
| Visual free area | 53 % | 53 % | 68 % | 68 % | 77 % | 77 % |
| Physical free area | 37 % | 37 % | 59 % | 59 % | 55 % | 55 % |

### Flow rates

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Feature | Pitch 75 | | Pitch 112 | | Pitch 150 | |
| **STD** | **+OPT** | **STD** | **+OPT** | **STD** | **+OPT** |
| Ce | 0.182 | 0.181 | 0.212 | 0.212 | 0.270 | 0.264 |
| K-factor intake | 30.19 | 30.52 | 22.25 | 22.25 | 13.72 | 14.35 |
| Cd | 0.200 | 0.197 | 0.270 | 0.266 | 0.313 | 0.308 |
| K-factor exhaust | 25.00 | 25.77 | 13.72 | 14.13 | 10.21 | 10.54 |

According to EN 13030

### Water resistance

|  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Velocity v (m/s) | Pitch 75 | | Pitch 112 | | Pitch 150 | |
| **STD** | **+OPT** | **STD** | **+OPT** | **STD** | **+OPT** |
| 0 | B | A | B | B | C | C |
| 0.5 | C | B | C | B | D | C |
| 1 | C | C | C | C | D | D |
| 1.5 | C | C | C | C | D | D |
| 2 | D | D | D | C | D | D |
| 2.5 | D | D | D | C | D | D |
| 3 | D | D | D | D | D | D |
| 3.5 | D | D | D | D | D | D |

According to EN 13030

### Strength calculation

According to EN 1990, EN 1991, EN 1999